| Date: Time: | Inspection Type | ☐ Routine ☐ Reinspection ☐ Complaint ☐ Outbreak investigation | ☐ Failed audit ☐ RMP review ☐ Reportable HCC result ☐ Reportable Legionella result |
| --- | --- | --- | --- |

| # Premises Details |  |
| --- | --- |
| Council ID for Cooling Water System (CWS) |  |
| CWS Current Risk Level |  |
| Total number of cooling towers in system |  |
| Unique Identification Number/s (UIN) |  |
| System Address |  |
| System Type |  |
| Make/Model |  |
| Location on site | ☐ Inside Location within building: ☐ Outside Details: |

| # Contact Details |  |
| --- | --- |
| Occupier’s name |  |
| Street Address |  |
| Postal Address |  |
| Mobile (24hr contact) |  |
| Email |  |
| ABN/ACN |  |

| Other Contacts | Name | Phone | Email |
| --- | --- | --- | --- |
| Building Manager |  |  |  |
| Water Treatment Company |  |  |  |
| Servicing Company |  |  |  |
| Water sampling contractor - micro |  |  |  |
| Water sampling contractor - chemical |  |  |  |
| Other |  |  |  |

| Urgent Contact Name | Phone | Alternative phone | Email |
| --- | --- | --- | --- |

OR

☐ Same as contact already listed, specify which: ___________________________________

Note: Urgent contact person/organisation must be able to provide required documentation to regulatory authorities (e.g. Council or NSW Health) within 4 hours of that documentation being requested via phone, e-mail and/or in person.

Indicate the following: Compliance ✓, Non-compliance x, or Not observed –

| Documentation |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Current RMP is in place. |  |  |  |  |  |
| Remedial actions in RMP are being addressed. |  |  |  |  |  |
| System is audited annually. |  |  |  |  |  |
| Monthly report is being completed. |  |  |  |  |  |
| Operation and maintenance manuals on site. |  |  |  |  |  |
| Electronic records available within 4hrs of request. |  |  |  |  |  |
| Display of UIN |  |  |  |  |  |
| UIN displayed on each cooling tower in approved manner |  |  |  |  |  |
| Microbial Sampling |  |  |  |  |  |
| Sampling is undertaken monthly and tested by a NATA accredited laboratory. |  |  |  |  |  |
| Sample is collected at least 72hrs after disinfection/decontamination/cleaning. |  |  |  |  |  |
| Sampling point on the return leg of chemical dosing. |  |  |  |  |  |
| Sample <100 000cfu/ml HCC and <10cfu/ml Legionella within last 12 months. |  |  |  |  |  |
| If Non-compliance: |  |  |  |  |  |
| - Council notified of reportable test results within correct timeframe. |  |  |  |  |  |
| - Remedial action taken as per Table 3.1/3.2 of AS/NZS 3666.3:2011. |  |  |  |  |  |
| If a water sample is collected during the inspection for testing, please indicate the sample location: ☐ Sample point; ☐ Basin; ☐ Other:. |
| Risk | Item Assessed |  |  |  |  |
| Stagnant water | CWS in continuous operation (i.e. not shut down for periods >48 hours) or otherwise drained, cleaned and kept dry if operated intermittently or seasonally. |  |  |  |  |
|  | No dead legs observed. |  |  |  |  |
|  | Other: |  |  |  |  |
| Nutrient availability and growth | CWS visibly clean with no signs of sludge, slime, sediment, biofilm, algae, fungi, rust, dust, dirt or foreign material. |  |  |  |  |
|  | CWS cleaned at frequency in accordance with RMP. |  |  |  |  |
|  | Direct sunlight prevented from entering wetted areas. |  |  |  |  |
|  | Other: |  |  |  |  |
| Poor water quality | Chemicals are automatically dosed, or automatic continuous water treatment system is installed |  |  |  |  |
|  | Adequate chemical volume remaining in chemical containers |  |  |  |  |
|  | Chemical supply lines clear from blockage and not kinked |  |  |  |  |
|  | Monthly servicing and water sampling completed. If servicing is outside of specified control range in RMP, appropriate corrective actions undertaken. |  |  |  |  |
|  | Other: |  |  |  |  |
| Deficiencies in CWS | Louvres in place, constructed of corrosion resistant material, fitted to prevent entry of contaminants, and in good working condition. |  |  |  |  |
|  | Fill in place, constructed of corrosion resistant material, designed for effective cleaning and in good working condition. |  |  |  |  |
|  | Drift eliminators in place, constructed of corrosion resistant material, and in good working condition. |  |  |  |  |
|  | Other |  |  |  |  |
| Location and access | No public access to the cooling tower. |  |  |  |  |
|  | Safe and easy access provided for cleaning, inspection and maintenance of the system. |  |  |  |  |
|  | CWS located away from air intakes, exhaust outlets, and passers-by. |  |  |  |  |
|  | Decommissioned cooling tower/s not in operation |  |  |  |  |
|  | Other: |  |  |  |  |

| Inspection outcome |  |  |
| --- | --- | --- |
| Inspection Result | ☐ Satisfactory | ☐ Not satisfactory |
| Further Action | ☐ No action required ☐ Verbal warning ☐ Warning letter ☐ Reinspection | ☐ Improvement Notice ☐ Prohibition Order ☐ PIN ☐ Charge for microbial sample |

Comments/Direction

| Officer details | Person spoken to onsite |
| --- | --- |
| Name: | Name: |
| Title: | Position: |
| Signature: | Signature: |
| Phone: | Phone: |
| Email: | Email: |